# Mircom FlexNet

NETWORK FIRE ALARM AND DETECTION SYSTEM

WITH EMERGENCY COMMUNICATION SYSTEM SPECIFICATION

# Notes about this specification

- These specifications are intended to provide guidance to the A&E community for fire alarm system design using MGC products.

- It is not intended that these specifications be used without a thorough review by an architect or a professional engineer.

- Mircom and its representatives take no responsibilities for any errors or omissions that may be present in the sample specification.

- Contact your local Mircom branch for assistance.

# PART 1 – GENERAL

## Scope

  - This specification describes an addressable/conventional fire detection and alarm signaling system. The control panel(s) shall include all required hardware, software and site specific system programming to provide a complete and operational system.

  - The control panel and all devices supplied shall in full compliance with all applicable codes and standards.

  - The features and capacities described in this specification are required as a minimum for this project.

## Design Performance Requirements

  - The control panel(s) shall be multi-processor based systems suitable for stand-alone or networked applications

  - Each panel shall be capable of functioning independently should it be disconnected from the network providing true Class A/Style 7 riser performance.

  - Each Panel shall support up to 9222 addressable points.

  - Each Panel shall support both addressable and conventional circuits.

  - Each Panel shall support up to 7 remote annunciators.

  - Each Panel shall support up to 29 SLC circuits, with up to 318 Addressable Points per SLC.

  - The system shall support up to 190,800 addressable points.

  - The system shall be capable of supporting up to 63 panels.

  - The system shall employ a proven Arcnet network technology.

  - The system shall be fully supervised, and shall monitor the integrity of all field wiring circuits and conductors and device placements.

  - The system shall provide multiple level passwords and flexible assignment of functions per password level.

  - The system shall have a built-in walk test feature.

  - The system shall be manufactured by an ISO 9001:2008 certified company.

  - The control panel(s) shall include all required hardware, software and site specific system programming to provide a complete and operational system.  The control panel(s) shall be designed such that interactions between any applications can be configured, and modified using software.

  - Each panel shall store copies of audio evacuation messages and tones.

  - The control panel operational priority shall assure that life safety takes precedence among the activities coordinated by the control panel

  - Each Network Panel shall incorporate Boolean control-by-event programming, including as a minimum AND, OR, NOT, and Timer functions.

  - The system shall be capable of downloading programming using Windows-based software while the system is fully operational, thus eliminating fire watch.

  - There shall be provision to store up to three different configurations in the system non-volatile memory.  Hot-Swapping between configurations shall be possible through menu operations from the front panel.

  - The system shall be capable of downloading programming for the entire network by connecting a laptop computer into any panel in the system.

  - The system can be configured in groups which allow the panels display to show all network activity, a group of panels or individual panel activity.

  - The system shall provide a RS-232C port for a printer. A configurable supervision option shall allow the supervision of the device connected to this port.

  - The system shall provide an Ethernet Port through a standard RJ-45 receptacle. It has provision for a connection to WAN using TCP/IP protocol.

  - Each Panel shall have built-in BACnet  support.

  - Each Panel shall have a built-in Ethernet port.

  - Each Panel shall be capable storing Two Event History Logs; 6000 event Alarm history log and a 6000 event log for All events.

  - Each Panel shall be capable of accommodating LCD display of up to 960 characters.

  - Each Panel shall be capable of XML based system device reporting.

  - An optional 3D graphical Monitoring and Control package shall be available.

  - The system shall incorporate one way and two way voice communications.

  - The system shall support up to three channels of audio signals simultaneously.

  - The audio system shall allow live voice communication and digitally recorded tones and voice messages to be sent to selected locations in the premises.

  - Audio system frequency response shall be a minimum of 400Hz to 4000Hz .

  - The audio system shall have Audio/Voice Evacuation with 520Hz capabilities.

  - The audio system shall allow live voice communication and digitally recorded tones and voice messages to be sent to selected locations in the premises.

  - Signals and zones selection shall be performed automatically in response to events as configured in the system.

  - The audio system shall have provision for manual overriding of signal and zones selections by the system operator.

  - All data and audio signals needed to be shared between sections of the audio system shall be transmitted in digital form over the same wire pair or fibre used for System network communication

  - Pre-recorded messages and tones must be stored in digital format in a non-volatile electronic memory.

### System Operation

  - In normal mode, the Control Panel(s) alpha-numeric display will indicate “normal condition”.

# Alarm Operation

  - If an alarm is initiated in any area of the building by the operation of a manual station, an automatic fire detector, or a sprinkler flow switch, the system shall initiate the following Alarm sequence of operations:

    - Indicate the point of alarm (zone/device description) on the LED display of the Control Panel(s).

    - Sound an audible buzzer at the Control Panel(s)

    - The Control Panel(s) buzzer can be silenced by pressing the Alarm acknowledge.

    - An LED's associated with the alarm zone shall be illuminated on the Control Panel(s)

    - Indicate the alarm condition by lighting the “COMMON ALARM” red LED at the Control Panel(s).

    - Every audible signal appliance shall sound in "general alarm" mode at a temporal rate until manually silenced

    - All alarm visual signals shall flash (i.e. strobes).

    - If silenced, the “SIGNAL SILENCE” light on the Control Panel(s) will illuminate.

    - If silenced, a subsequent alarm will re-activate the signals.

    - Type, location, time and date of alarm condition shall be recorded in the Alarm Event History.

    - Event shall be printed on the system printer, where applicable.

    - All designated fans shall be automatically turned off.

    - All designated smoke control fans shall be automatically turned on.

    - Doors normally held open through magnetic door holders shall be released.

    - Doors normally locked by magnetic locking devices shall be released.

    - Initiate Emergency Elevator Recall.

    - If alarm is initiated by an automatic detector on the floor of recall, activate Alternate Floor recall relay, where required by code.

    - Activate connection to monitoring system (by others) to transmit a signal to fire department or approved central station.

    - An alarm in the Elevator Shaft or Elevator Machine Room shall activate a relay connected to the Elevator Controller.

    - An Alarm can be reset by pressing the “RESET” button on the Control Panel(s)

## Supervisory Operation

  - If a supervisory signal is initiated in any area of the building by the operation by sprinkler/fire pump supervisory device , guest unit smoke or CO detector,  duct smoke detector or elevator shunt trip, the system shall initiate the following Supervisory sequence of operations:

- Indicate the supervisory point (zone/device description) on the LCD display of the Control Panel(s)

- Sound an audible buzzer at the Control Panel(s)

- The Control Panel(s) buzzer can be silenced by pressing the supervisory acknowledge switch.

- Indicate the supervisory condition by lighting the “COMMON SUPERVISORY” amber LED at the Control Panel(s)

- Type, location, time and date of supervisory condition shall be recorded in the System Event History.

- Event shall be printed on the system printer, where applicable.

- Activate connection to monitoring system (by others) to transmit a signal to fire department or approved central station.

- The Control Panel(s) buzzer can be silenced by pressing the supervisory acknowledge switch.

- An LED's associated with the supervisory zone shall be illuminated.

- Event shall be printed on the system printer, where applicable.

- Activation of any Guest Suite smoke or CO detector shall be displayed on the panel(s) main LCD display individually as a supervisory and activate the sounder base(s) within the Guest Suite.

## Trouble Operations

  - If a trouble signal is initiated in any area of the building by an open/short /ground circuit fault, battery/power failure, communication failure, or any removal of the systems panel/remote annunciator component, the system shall initiate the following Trouble sequence of operations.

- Indicate the type of trouble on the LCD display of the Control Panel(s).

- Sound an audible buzzer at the Control Panel(s)

- The Control Panel(s) buzzer can be silenced by pressing the supervisory acknowledge switch

- Indicate the trouble condition by lighting the “COMMON TROUBLE” amber LED at the Control Panels

- Type, location, time and date of trouble condition shall be recorded in the System Event History.

- Event shall be printed on the system printer, where applicable.

- Activate connection to monitoring system (by others) to transmit a signal to fire department or approved central station.

- The Control Panel buzzer can be silenced by pressing the acknowledge switch at the control panel

## One way Audio communication

  - The audio system control equipment shall comprise an audio controller, Paging Microphone, FF telephone master handsets, page/telephone selector switches and appropriately sized amplifiers.

  - Paging features included the following:

- All-Call: Selects all zones for live paging.

- Warden page: Allows the use of a remote telephone for live paging

- Page to Evac: Redirect the paging signal to the zones getting evacuation signals.

- Page to Alert: Redirect the paging signal to the zones getting alert signals.

- All-Call Minus: Prevents selected zones from getting live paging.

  - Where the premises are divided in zones with distinct speaker circuits, a Page selection switch shall be provided to connect each zone.

  - The audio system shall allow live voice communication and digitally recorded tones and voice messages to be sent to selected locations in the premises.

## Two-way firefighter’s Telephone System

  - The firefighter’s telephone system included the following:

- Capable of five party telephone conversations.

- The firefighter’s telephone system shall provide individual call-in and trouble indication for telephone zones.

- Initiate a call to other Master handsets in the system.

  - The firefighter’s telephone system shall have the capability for installation of additional Master handset modules and selection switches at any control panel or remote annunciator

## Submittals

Prior to installation, submit fabrication drawings, material lists and equipment submittals (shop drawings) for approval in accordance with the following:

  - Complete description (manufacturer’s cut sheets) data indicating ULC listing for all network components including the Control Panel(s).

  - Complete sequence of operation of all functions.

## Equipment References and Standards

  - The equipment and installation shall comply with the provisions of the following codes and standards unless the authority having jurisdiction has adopted an earlier version:

- All applicable National and/or Provincial building codes recognized at the time of installation.

- National or Provincial Electrical Safety Code

- CAN/ULC-S524, Installation of Fire Alarm Systems.

- CAN/ULC-S525, Audible Signal Devices for Fire Alarm Systems.

- CAN/ULC-S526, Visual Signal Devices for Fire Alarm Systems.

- CAN/ULC-S527, Control Units for Fire Alarm Systems.

- CAN/ULC-S528, Manual Pull Stations for Fire Alarm Systems.

- CAN/ULC-S529, Smoke Detectors for Fire Alarm Systems.

- CAN/ULC-S530, Heat Actuated Fire Detectors.

- CAN/ULC-S531, Smoke Alarms.

- CAN/ULC-S536, Inspection and Testing of Fire Alarm Systems.

- CAN/ULC-S537, Verification of Fire Alarm Systems.

- CAN/ULC-S541, Speakers for Fire Alarm Systems.

- CAN/ULC-S548, Devices & Accessories for Water Type Extinguishing Systems.

- All work shall comply with the requirements of the Local Authorities Having Jurisdiction.

# PART 2 – PRODUCTS

## ACCEPTABLE MANUFACTURERS

  - The system specified herein is based on equipment and design of Mircom Technologies Ltd. Flex-Net series network fire alarm system.

## Main Network Board (Model FX-2000N)

  - The control panel shall provide three dry contacts for the reporting of common trouble, common alarm and common supervisory conditions.

  - Dry contacts shall provide form C (SPDT) connection and be rated at 1A at 24VDC

  - The control panel shall have one SLC interface supporting up to 159 addressable fire detection devices and 159 addressable input or output modules

  - The control panel shall provide one 24 VDC @ 1.7A special applications output for auxiliary equipment. This auxiliary equipment output shall be power limited and equipped with an auto-resettable over-current protection.

  - The control panel shall have a 12 Amp main power supply.

  - The control panel shall provide a 24VDC, 400mA output for devices and equipment such as four wires detectors. This output shall be shut down when the reset button shall be activated.

  - The control panel shall include four NAC lines capable of 1.7 amperes each at 24VDC or 5 Amperes total.

  - The control panel shall provide connectors for Class A or Class B connection for each NAC output

  - Each control panel shall have a capacity of up to 16 conventional input/output adder modules.

  - Where additional power is required, the Mircom INX-10A power supplies shall be used.

## Main Display (Model DSPL-420)

  - The display shall be a 4 line by 20 character backlit LCD display or optional 24 lines by 40 character backlit LCD display.

  - The following panel status shall be indicated by individual LEDs:

- System Power (green LED). Illuminated when main AC power is within specs.

- Alarm queue (red LED). Flashes when a new alarm has been received.

- Trouble queue (yellow LED). Flashes when a new trouble has been received.

- Supervisory queue (yellow LED). Flashes when a new supervisory event has been received.

- Monitor queue (yellow LED). Flashes when a new trouble has been received.

- Ground Fault (yellow LED). Illuminated when a ground fault has been detected.

- CPU Fault (yellow LED). Illuminated when processor is unable to perform its tasks.

  - The queues LED shall turn to steady ON when all related events have been reviewed by the system user through the queues navigation switches.

  - The following functions shall be controlled by dedicated switches:

- Alarm Silence.

- Fire Drill

- Alarm Acknowledge (“automatic Alarm signal cancel”).

- Alarm Reset.

- Trouble Silence.

- Lamp Test.

- On screen menu key.

- Menu Navigation keys ( left , right , up and down screen scroll)

- Info key for getting more information on displayed event.

- OK key to accept menu items.

- Cancel key to exit menu items.

- Queue navigation and acknowledge keys (one for each queue).

## Programmable Input Switch Display Adder (Model IPS-2424DS)

  - The input switch adder module shall be used to provide 24 programmable switches for functions such as Zone bypass. Each switch shall be equipped with a yellow LED for indicating a trouble condition and with a dual color LED (red and yellow) to indicate an active condition. Active LED color shall be configurable according to the requested function. It shall have on-site labelling capacity for each switch.

## Programmable LED Display Adder (Model RAX-1048TZDS)

  - The LED display adder shall be used to provide 48 programmable pairs of  LED indicators, one yellow and one red with on-site labelling capability.

## Programmable Fan Damper Adder (Model FDX-008)

  - The Fan Damper display adder shall be used to provide fan damper control. Each adder shall provide 8 switches with three non-momentary positions: OFF - AUTO - MAN control. LEDs should be provided to indicate the state of each fan controlled by a switch and to report eventual trouble condition if the fan system has proving capability. Model FDX-008KI adder shall be used where one key-switch activated zone is required.

## Network Interface Module (Model FNC-2000)

  - The control panel shall have provision for the installation of a network interface card. This shall enable up to 63 control panels to work together in a peer to peer high speed network. Using the recommended wiring, the network shall work with distances of up to 4000ft between control panels.

  - Overall connection between panels must be selectable to be open ended (class B) or looped back (class A).

  - Where loop connection is selected for the network, a single short, open or ground fault shall be detected but shall not affect system operation. When multiple wiring faults result in isolation of sections of the network, each individual section shall continue to operate normally without compromising alarm detection and annunciation in the related zones.

## SLC Modules (Model ALCN-792M and ALCN-792D)

  - Additional SLC circuits shall be supported through adder master and daughter board quad loop controller modules. Each master shall have a dedicated central processor unit (CPU) and shall support two fully loaded SLC lines. The daughter shall provide two additional SLC lines.

  - A list of acceptable devices is provided in the section covering initiating devices.

  - SLC lines shall be capable of Class B (single ended) or Class A (looped) wiring arrangement without affecting the total number of SLC lines  or devices supported by the system

## Control Panel Conventional Adder Modules

  - Conventional input devices can be support by the conventional input circuit adder modules (model DM-1008A) mounted inside the control panels. Each module shall provide four Class A detection or eight Class B circuits.  Up to 128 conventional Class B circuits can be connected to a control panel.

  - Additional NACs circuits can be support by the NAC circuit adder modules (model SGM-1004A) mounted inside the control panels. Each module shall provide four outputs with connectors for Class A or Class B wiring of each circuit.

  - Programmable dry contact relays can be support by the relay circuit adder modules (model RM-1008A) mounted inside the control panels. Each module shall provide 8 form C (SPDT) contacts rated at 1A at 24VDC and shall be individually programmable.

## Polarity Reversal/ City Tie Module (Model PR-300)

  - The polarity reversal/city tie module provides the system with a supervised city tie connection (24VDC/200mA max) and a polarity reversal connection (24VDC (open circuit),8mA max (shorted) )It shall be compact and shall be mounted inside control panel.

  - The control panel shall have provision for disabling the unit for system testing.

## UDACT Communications Module (Model UDACT-300A)

  - The UDACT digital Communication Module allows the system to transmit addressable point information to a central station. It shall be compact and shall be mounted inside control panel.

## Main Power Supply

  - The control panel main power supply shall be 120VAC 60Hz and shall have over-current protection.

  - The quality of the AC power shall be monitored by the control panel. There shall be an automatic transfer of power to the back-up power source when AC voltage falls under a level where panel performance is compromised.

## Standby Power

  - Sealed lead-acid batteries shall be used to provide 24VDC standby power.

  - The batteries shall be sized according to system requirements calculated in the installation manual of the control panel.

  - The battery charger shall provide full recharge of the selected batteries as per ULC requirements.

  - The battery charger shall be monitored for integrity and a trouble shall be indicated if battery charging is no more possible or if the battery is disconnected.

## Audio Controller (Model ANC-5000)

  - The audio controller shall handle the control and supervision of the audio sub-functions and shall provide the required stored alarm messages or tones generation.

  - The audio controller shall perform continuous supervision of amplifiers, speaker circuits and other audio functions. Should a problem occur, the audio system shall report the specific information as to the type of failure (e.g., microphone trouble, tone trouble, etc.).

## Microphone Module (Model QMP-5101N and QMP-5101NV)

  - The Microphone module shall be used to provide live paging capability on the audio system

  - The module shall provide a hand-held microphone with a push-to-talk switch and a coiled cord.

  - There shall be a recess in the module enclosure to store the microphone when not in use.

  - Microphone connections and wiring shall be supervised and a trouble shall be indicated in case of failure.

  - The module shall have the following switches:

- All-Call: Selects all zones for live paging.

- Warden page: Allows the use of a remote telephone for live paging.

- Page to Evac: Redirect the paging signal to the zones getting evacuation signals.

- Page to Alert: Redirect the paging signal to the zones getting alert signals.

- All-Call Minus: Prevents selected zones from getting live paging.

- Page cancel: Cancels all current zone selection

  - The module will have the following LED indicators:

- Green activation confirmation LEDs for All-Call, Warden Page, Page to Evac, Page to alert and All-Call Minus functions.

- Green LED labelled “AC on”.

- Green LED for indication that the paging call can be initiated labelled “Page ready”.

- Yellow LED for indication of off-normal conditions: Common trouble, amplifier trouble and microphone trouble.

## Paging and Telephone Selectors Switches

## (Model QAZT-5302DS)

  - The input switch adder module shall be used to provide 24 programmable switches for functions such page zone selection, firephone handset selections, and digitized message selection.

  - Each switch shall have two corresponding LEDs: The lower one shall be a yellow LED for indication of troubles on speaker lines or on amplifiers related to the zone. The top one shall be a green LED for indication of paging selection and activation in the zone.

  - Where multiple microphones are used, a priority system shall allow control of the paging function as per an order determined by the authority overseeing the installation.

## Amplifiers (Model QAA-5000 Series)

  - For maximum reliability, each speaker line shall be driven from a distinct amplifier

  - The amplifiers shall provide output for speaker circuit loads of 60, 30, or 15 Watts.  Output voltage shall be for 25VRMS or 70VRMS operation. Speaker circuits can be either Class B (open ended) or Class A (looped) wiring.

  - Amplifiers shall be self-contained with an audio amplifier being present along with speaker circuit supervision  circuitry on the same unit

  - Amplifier connections shall be of the plug-in type.

  - Amplifiers should have power-limited output and have automatically resettable current limit and short-circuit protection circuitry.

## Control Panel Firefighters Master Handset (Model QMT-5320N)

  - A Master handset module shall be present at the control panel providing the system user interface.

  - The Master handset module shall provide the following switches:

  - Warden page: Allows the use of a remote telephone for live paging.

  - Deselect All: Cancels all telephone zones selection

  - Call control: Initiate a call to other Master handsets in the system.

  - The Master handset module shall provide the following switches:

  - A yellow LED for trouble indication

  - A green LED for incoming calls indication.

  - A green LED to indicate initiation of call control function

## Enclosures

  - The enclosures back-boxes and doors must be made of heavy gauge steel. They must be suitable for flush or surface mounting.

  - All enclosures doors must be equipped with a key lock. On all enclosures where user access is allowed, a dead-front cover must be used for protection.

## Printer (Model PTR-2000-1)

  - A printer shall be provided to record events and status logging. It shall be a dot matrix type with continuous tractor feed and internal menu driven program.

  - It shall be provided with a RS-232C serial interface suitable for 9600bps data rate.

## Remote Annunciators (Model RAXN-LCD or RAXN-LCDG)

  - The remote annunciators shall provide the same display, controls and indicators as the control panel’s main display.

  - The remote annunciators shall use the same RAX-1048TZDS display adder modules as the control panels to provide programmable switches and LED indicators.

  - The remote annunciators shall be able to accommodate the same paging microphone modules and master telephone modules used on the control panel.

  - Remote annunciators’ enclosures shall be made of heavy gauge steel with a lockable door. They shall be suitable for recessed or surface mounting as applicable.

Global Event Graphical Workstation (OPENGN)

General:

2.70	The global event graphical workstation shall run the Mircom Open Graphic Navigator (OpenGN) software package.

2.71	The monitoring and control graphical workstation shall communicate with the fire alarm network(s) via supervised Ethernet port using IP communications protocol with full command and control capability.

2.72	OpenGN is UL 864 listed for control when installed on a UL certified computer.

2.73	OpenGN is password protected to operate common control functions from the Workstation including acknowledging, silencing, and resetting of fire alarm functions

2.74	Capable of generating reports in multiple formats with ability to filter by building/area, device type, and/or activation type

2.75	Capable upon receipt of any event to activate an audio WAV file over the workstation speakers alerting the operator to an event, and providing detailed textual instructions on a ‘per device’ basis.  Additionally, a visual graphical indication color coded for the event type shall appear for the affected device

2.76	Support multiple fire alarm Networks Systems via Ethernet using IP protocol communications. Networks can be monitored independently and all information shall be stored locally in a database format. Events can be filtered based on trouble and/or alarm activations.

2.77	Shall be able to activate preset switches on the FACP to perform operations related to fire system control and maintenance

2.78	Graphical screens shall be provided to select a virtual switch

2.79	Must allow for master node for control and slave nodes for auxiliary monitoring

Operator interface:

2.80	The operator interface shall manage and configure the different screen (window) layouts for the operator System Control to be display simultaneously on the screen.

2.81	The operator interface shall provide support for dual monitor mode.

2.82	It shall be possible to limit functions to access groups so that they load when a user from that access group logs in.

2.83	User authentication shall be provided using access groups with defined permissions and with support of multiple user accounts per access group.

Event list display:

2.84	All events shall be displayed in the order of priority and remain until they are acknowledged.

2.85	 Each event and notification shall be color-coded.

2.86	The event type, description, location, date and time and count information shall be displayed for each event in columns on each tab.

2.87	 Once the event has been acknowledged, a visual indicator showing the event has been acknowledged shall be presented to the operator and logged to the database.

2.88	The current events tab shall display all of the events that have taken place in the system up to a maximum of 1,000 events.

2.89	 All other events shall be stored in the database and accessible via a separate “event log” window. Extensive event logging up to 500,000 events with status notations for report customization.

2.90	The following colour Coding of events and notifications shall be used

a) Red – Mass Notification or Fire Alarms.

b) Orange  – Supervisory or Security Alarm

c) Yellow – Troubles

d) Blue – Monitor Points or Security Points

e) Green – Restored to normal.

Workstation Event Logging and Reports Print Filter:

2.91	Filters shall be made available through configuration for events to be printed or reported from the workstation. The following filters shall be provided:

a) Alarms,

b) Supervisory,

c) Monitor,

d) Troubles and

e) Security events

f) Time of Day

g) Location of the Event

The following pre-programmed reports shall be available:

2.92	Alarm Report – Print only Alarm events.

2.93	Alarm and Supervisory Report – Print only Alarm and Supervisory events.

2.94	Maintenance Report – Print all events.

2.95	Location Report – Print all events of a specific building/floor

2.96	Time Period Report – Print all events from a date range

Facility 3D Event Management Interface:

2.97	The 3D event management interface shall display facilities organized by building, floor, and device. Upon event activation it shall:

2.98	Provide the opportunity to display the device custom take action message with a minimum of 500 characters. The custom message shall provide instructions to the operator on what to do, information on the event/device and possible hazards.

2.99	Provides 3D visual representation of new device status.

On Screen Controls:

2.100	The system shall provide on-screen buttons for;

a) Acknowledge,

b) Signal Silence,

c) Buzzer Silence,

d) Fire Drill,

e) Total Evac,

f) Reset, and

g) Silence Workstation

h) Network View

i) 3D View

j) 2D View

Facilities rendering:

2.101	The system shall display site plan vector rendering of campus, building or facility, with optional vector rendering of building profile and every level of building floor plan map.  Operator shall be able to zoom to any desired level without pixilation when a vector based input file is used for the campus, building or floor.

2.102	The buildings of the campus shall be presented as a set of stacked 2D floor plans to create a transparent 3D image of the building

2.103	Devices shall be visible through the transparent floors when looking “through the top” of a building in birds eye view camera position

2.104	Device activation animations shall also be visible through the transparent floor plans as above from ‘birds eye view’ camera position

Optional browser window:

2.105	The software shall have the ability to customize each Access Level with the ability to limit system restrictions and shall be password protected. It shall provide a minimum of 128 users with access levels.

Graphical maps and floor plans:

2.106	It shall be possible to import graphical floor plans from several different graphic file formats.

2.107	Drawing display shall allow for zoom out to full floor view or zoom in to individual device location. It shall be possible for the operator to manually zoom down, using the PC mouse or multi-touch, to any portion of a vector-based graphic without aliasing, artefacts, or pixilation of the image. Systems using a static two picture method for zooming are unacceptable.

2.108	Preset-only zoom levels shall not be considered equivalent.

2.109	It shall be possible to place buildings in their respective geographic location on the campus layout plan.

2.110	The system must have available floor plan legend to identify locations on floor plan key view.

2.111	There shall be toggle buttons on screen for all drawing levels that allow instant migration to the previous and next building compared to the building currently being displayed on screen.

2.112	There shall be toggle buttons on screen for all drawing levels that allow instant migration to the previous and next floor compared to the floor currently being displayed on screen.

2.113	The system shall provide the following Floor Plan features:

a) All Exterior and Interior Walls furnished as per architectural drawings

b) Door swings.

c) Window locations.

d) Room number and designation of occupancy.

e) All initiating device locations.

PC requirements:

2.114	Operating software shall be Microsoft Windows 7 Professional, 64 bit.

a) Intel© CoreTM i7-4790Processor.

b) 16GB RAM 1600 MHz DDR3.

c) AMD Radeon 2 GB R7 250.

d) Audio sound.

e) 10/100/1000 Ethernet Port.

f) 500GB Hard Drive.

g) 24X DVD-R/W, DVD+RW, CD-R/W.

h) Computer hardware for Control shall be UL864 listed.

Video display requirements:

2.115	The video display shall be 19 inches or more LCD display monitor with built-in audio speakers and touch screen control with multi-touch operation.

2.116	Touch-screen Video display for Control shall be UL 864 listed.

Power supply requirements:

2.117	The workstation and display shall be connected to a UPS System sized to provide back-up support for ___ (minutes) (hours) of operation.

## NAC Booster Power Supply (Model INX-10A)

  - It shall have an AC power input rated for either 120VAC 60Hz or 220VAC 50Hz operation.

  - The batteries shall be sized according to system requirements calculated in the installation manual.

  - The battery charger shall provide full recharge of the selected batteries as per UL requirements.

  - The battery charger shall be monitored for integrity and a trouble shall be indicated if battery charging is no more possible.

  - The NAC booster power supply shall provide five power-limited outputs rated at 2.5A @ 24VDC. Outputs shall be selectable to be used for NAC (active during alarms) or power supply duty (active at all time).

  - Outputs configured as NAC shall be configurable for Steady, Temporal Code, California Code and March Time rates.

  - The NAC booster power supply shall provide a SLC interface allowing it be controlled as an addressable intelligent device.

  - The outputs configured for NAC duty shall also be controllable by analog ON/OFF inputs if the SLC interface is not used.

  - The NAC booster power supply shall have built-in protocols for industry-standard devices such as horns and strobes from Amseco, Gentex, System Sensor and Wheelock.

  - Configuration of the NAC booster shall be done through DIP switches only.

## Addressable Detectors (Mircom 200 Series)

  - All detectors shall be of the detachable head, twist-lock and plug-in type. The field connections shall be made on a Mircom 200 Series base equipped with self-wiping contacts for the connection of the detector head.

  - Addressable devices should use easy to read rotary switches for address selection.

  - Each detector head occupies any one of at least 159 possible Intelligent Sensor addresses on the signaling line circuit (SLC) loop. It responds to regular polls from the system and reports its type and status.

  - Detectors shall have an integral LED for alarm indication.

  - Mircom 200 Series bases with remote alarm indicators, relays or audible alarm indicators options shall be provided where required.

  - Detectors should have a built-in test feature.

  - MIX-2251APA Photoelectric smoke detector shall be analog intelligent addressable type and use light scattering principle (light emitting diode source; light sensing photo diode receiver). They shall be easily cleanable and corrosion resistant.

  - MIX-2251TAPA smoke detector shall be an addressable intelligent photoelectric smoke detector and a 135 deg. F fixed thermal sensor in a single sensing device.

  - MIX-2251TMAPA intelligent multi-criteria acclimating detector shall monitor a space with a minimum of photoelectric and thermal technologies in single sensing device. The detector shall include the ability to adapt to its environment and choose appropriate sensing settings. The device shall be able to indicate distinct smoke and heat alarms.

  - MIX-5251APA 135 deg. F Fixed temperature thermal detectors shall be shall be of analog intelligent addressable type with thermistor sensing circuit.

  - MIX-5251RAPA 135 deg. F Fixed temperature with rate of rise thermal detectors shall be of analog intelligent addressable type with thermistor sensing circuit.

  - MIX-5251HAPA 190 deg. F Fixed temperature thermal detectors shall be of analog intelligent addressable type with thermistor sensing circuit.

  - DNR/DNRW Photoelectric duct smoke detector housings shall be compatible with MIX-2251APA or MIX-2251BRA (remote test switch compatible) photo-electric detectors and shall work with air velocity rates of 100ft/min to 4000ft/min. Installation of sampling tube shall require no tools and shall be possible from the front or the back of the detector.

Advanced Multi-Criteria Fire/CO Detector (MIX-COSAPA)

  - Advanced Multi-Criteria Fire/CO Detector shall be a Mircom MIX-COSAPA addressable advanced multi-criteria smoke detector with a separate signal for carbon monoxide (CO) detection per UL 2075 standards.

  - The detector shall provide address-setting means on the detector head using rotary switches. Because of the possibility of installation error, systems that use binary jumpers or DIP switches to set the detector address are not acceptable. The detector shall also store an internal identifying code that the control panel shall use to identify the type of detector. Systems that require a special programmer to set the detector address (including temporary connection at the panel) are labor intensive and not acceptable.

  - Each detector head occupies any one of at least 159 possible Intelligent Sensor addresses on the signaling line circuit (SLC) loop. It responds to regular polls from the system and reports its type and status.

  - The detector shall be comprised of four sensing elements, including a photoelectric (light- scattering) particulate sensor, an electrochemical CO sensor, a daylight-filtered infrared (IR) sensor and solid state thermal sensor(s) rated at 135°F (57.2°C).

  - The device shall be able to indicate distinct smoke and heat alarms.

  - The advanced multi-criteria detection device shall include the ability to combine the signal of the photoelectric signal with other sensing elements in order to react quickly in the event of a fire situation.

  - It shall also include the inherent ability to distinguish between a fire condition and a nuisance alarm condition.

  - The detector shall be capable of selecting the appropriate sensitivity levels based on the environment type (office, manufacturing, kitchen, etc.) in which it is installed, and then have the ability to automatically change the setting as the environment changes.

  - The CO detector component shall be capable of a functional gas test using a canned test agent to test the functionality of the CO sensing cell.

  - The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms. The device shall provide unique signals to indicate when 20 percent of the drift range is remaining, when 100 percent of drift range is used, and when there is a chamber fault to show the unit requires maintenance.

  - The detector shall indicate CO trouble conditions, including six months of sensor life remaining and sensor life has expired.

  - The detector shall be plug-in mounted into a twist-lock Mircom APB200COA base.

Advanced Intelligent Sounder Base (APB200COA)

  - The sounder base appliance shall be model APB200COA.

  - The sounder base shall be listed to CAN/ULC-S529 and CAN/ULC-S525. The sounder shall have an option to switch between a temporal three-pattern, temporal four-pattern, non-temporal (continuous) or march time pattern.

  - The sounder base shall offer two volume levels. The alarm current shall not exceed 140 mA at 16 VDC.

  - The sounder base shall operate between 10% and 93% relative humidity.

  - A pre-wire mounting plate shall be used for mounting products. The wiring shall terminate at the pre-wire mounting plate.

  - The sounder base shall have the ability to synchronize with notification devices without the use of added accessories. A manual locking feature shall be available to prevent removal of the attached sensor head.

  - When used with the MIX-COSAP Advanced Multi-Criteria Fire/CO detector the APB200COA series sounder base occupies two of at least 159 possible module addresses.

## Manual Pull Stations (Mircom series MS-700)

  - Intelligent Addressable Advanced Protocol Manual Pull Stations (Mircom series MS-700)

  - The Manual Pull Station shall be intelligent addressable advanced protocol and be compatible with other intelligent addressable advanced protocol devices.

  - Manual Pull Station shall be Mircom MS-710AD dual action station.

  - The Manual Pull Station’s integrated intelligent addressable advanced protocol module shall provide address-setting means on the module using rotary switches. Because of the possibility of installation error, systems that use binary jumpers or DIP switches to set the module address are not acceptable. The modules shall also store an internal identifying code that the control panel shall use to identify the type of input. Systems that require a special programmer to set the module address (including temporary connection at the panel) are labor intensive and not acceptable. Each module occupies any one of at least 159 possible addresses on the SLC loop. It responds to regular polls from the system and reports its type and status.

  - Operating instructions shall be in raised lettering and the unit shall be constructed of high quality die-cast metal and finished in red enamel paint to provide quick identification. Double action Manual Pull Station shall require pushing a bar first to free the handle. Bar shall be marked “PUSH BAR”. Then pulling the handle marked “PULL HANDLE”. Pulling the handle shall initiate immediate operation of the intelligent addressable module. MS-710AD Manual Pull Station shall meet ADA requirement of 5 lb. maximum pull force.

  - The pull station shall require a Mircom CAT-30 key to restore the handle the normal position.

## Intelligent Addressable Advanced Protocol Modules

  - The input modules shall be used to monitor the status of alarm supervisory and monitor dry contacts. MIX-M500MAPA modules shall be used where Class A wiring or screw terminals are mandatory. MIX-M501MAPA shall be used where Class B wiring and pig-tail connections are acceptable. MIX-M500DMAPA shall be used where two separate Class B circuits must be monitored.

  - Contact monitoring circuit shall have three states: Normal when circuit is terminated with rated end of line resistor, alarm when the circuit is shorted and trouble/supervisory when the circuit is opened.

  - Each module occupies any one of at least 159 possible addresses on the SLC loop. It responds to regular polls from the system and reports its type and status.

  - Short-circuit isolators for SLC line shall be Mircom M500XA . They shall be used to isolate SLC sections made of up to 25 devices from a short-circuit happening in another zone. Short-circuit shall be automatically detected and isolated. The M500XA shall restore loop connection upon removal of fault.

  - Addressable relay module shall be Mircom MIX-M500RAPA. It shall provide one DPDT set of electrically isolated contacts. Contact rating shall be 2 amps at 24 VDC or 0.5 amps at 120 VAC.

  - Addressable output module with supervision shall be Mircom MIX-M500SAPA. It shall provide one DPST set of contacts. Output side shall be supervised when contact is set to open (reset) condition. When activated, the contacts shall be connected to the input port.

  - Contact rating shall be 2 amps at 24 VDC.

## Conventional Smoke Detectors

  - The smoke detector shall be one of the models listed below as required and as specified on the project plans:

  - Model C2W-BA  2 wire direct smoke detector, photoelectric type

  - Model C2WT-BA  2 wire direct smoke detector, photoelectric type, complete with thermal detector

  - Model C2WTR-BA  2 wire direct smoke detector, photoelectric type, complete with thermal detector and relay contacts

  - Model C2WTA-BA  2 wire direct smoke detector, photoelectric type, complete with thermal detector and audible sounder

Advanced Multi-Criteria Fire/CO Detector (MIX-COSAPA)

  - Advanced Multi-Criteria Fire/CO Detector shall be a Mircom MIX-COSAPA intelligent addressable advanced protocol multi-criteria smoke detector with a separate signal for carbon monoxide (CO) detection per UL 2075 standards.

  - The detector shall provide address-setting means on the detector head using rotary switches. Because of the possibility of installation error, systems that use binary jumpers or DIP switches to set the detector address are not acceptable. The detector shall also store an internal identifying code that the control panel shall use to identify the type of detector. Systems that require a special programmer to set the detector address (including temporary connection at the panel) are labor intensive and not acceptable. Each detector head occupies any one of at least 159 possible Intelligent Sensor addresses and any one of at least 159 Intelligent Module addresses on the signaling line circuit (SLC) loop. It responds to regular polls from the system and reports its type and status.

  - The detector shall be comprised of four sensing elements, including a photoelectric (light- scattering) particulate sensor, an electrochemical CO sensor, a daylight-filtered infrared (IR) sensor and solid state thermal sensor(s) rated at 135°F (57.2°C).

  - The device shall be able to indicate distinct smoke and heat alarms.

  - The advanced multi-criteria detection device shall include the ability to combine the signal of the photoelectric signal with other sensing elements in order to react quickly in the event of a fire situation.

  - It shall also include the inherent ability to distinguish between a fire condition and a nuisance alarm condition.

  - The detector shall be capable of selecting the appropriate sensitivity levels based on the environment type (office, manufacturing, kitchen, etc.) in which it is installed, and then have the ability to automatically change the setting as the environment changes.

  - The CO detector component shall be capable of a functional gas test using a canned test agent to test the functionality of the CO sensing cell.

  - The detector shall be capable of automatically adjusting its sensitivity by means of drift compensation and smoothing algorithms. The device shall provide unique signals to indicate when 20 percent of the drift range is remaining, when 100 percent of drift range is used, and when there is a chamber fault to show the unit requires maintenance.

  - The detector shall indicate CO trouble conditions, including six months of sensor life remaining and sensor life has expired.

  - The detector shall be plug-in mounted into a twist-lock Mircom APB200 Series base: APB200S or APB200-LF (Low Frequency).

Advanced Intelligent Sounder Base – Low Frequency

(APB200-LF)

  - The low frequency sounder base appliance shall be Mircom model APB200-LF.

  - The low frequency sounder base shall be listed to UL 268 and UL 464. The low frequency sounder shall have an option to switch between a temporal three-pattern, temporal four-pattern, non-temporal (continuous) or march time pattern.

  - The low frequency sounder base shall offer two volume levels. The alarm current shall not exceed 140 mA at 16 VDC The low frequency sounder base shall operate between 10% and 93% relative humidity.

  - The low frequency sounder base shall be designed to meet the NFPA 72 sleeping space requirement to produce a fundamental frequency of 520 Hz +/- 10% with a square wave or its equivalent.

  - A pre-wire mounting plate shall be used for mounting products. The wiring shall terminate at the pre-wire mounting plate.

  - The low frequency sounder base shall have the ability to synchronize with notification devices without the use of added accessories. A manual locking feature shall be available to prevent removal of the attached sensor head.

## When used with the MIX-COSAP Advanced Multi-Criteria Fire/CO detector the APB200 series sounder base occupies one of at least 159 possible module addresses.

## Signalling Devices:

  - Signalling devices other than speakers shall be compatible with the system as per the latest revision of Mircom document LT-1023.

  - Strobes intended for Fire-Alarm signalling, shall have a clear lens and shall have a white housing with red “FIRE” lettering

  - Speaker and strobes for Fire-Alarm shall operate from either 25VRMS or 70VRMS and offer taps at 1/8W, 1/4W, 1/2W, 1W and 2W.  Speakers shall produce 77 to 88dBA at 10ft over the power range. The frequency response shall equal or exceed the 400 to 4000Hz range.

  - Speakers shall be available with red or white finish for Fire-Alarm applications.

  - For locations requiring a strobe, a unit integral to the speaker shall be supplied with either selectable 15/30/75/95, 115/177 or 135/185 candelas ranges or a fixed 1575 (75 on axis) candela value. Strobes light sources shall be a Xenon tube or LED with a clear lens and they shall be capable of synchronization. The speaker unit shall be identified with “FIRE” in red or white letters contrasting with housing color.

## Control Panel Programming

  - Programming of the system shall be executed by an authorized technician.

  - Update firmware to latest available version at project completion.

  - The system shall be expandable and reprogrammable at any time up to system’s maximum capacity.

  - Operating system shall be field programmable for program changes and shall not require any factory modifications.

# PART 3 EXECUTION

## Installation - General

  - The fire alarm system shall be installed in accordance to the latest revision of CAN/ULC-S534 “Standard for the Installation of Fire Alarm Systems” and

  - Install and connect fire alarm system components as shown on drawings and as required to fire protect the building.

  - Review with the system manufacturer the requirements for wiring installation methods, sequence of operation of system, CACF annunciator requirements including nomenclature and any other pertinent requirements, and advise the engineer of any requirements that contradict or deviate from the Contract Documents. Review also the requirements for interconnections to other building systems, as applicable.

  - The sequence of operation provided in this specification is an outline for tendering, with exact requirements to be confirmed and programmed to the requirements of the fire plan, authority having jurisdiction, and Consultant.

  - The system shall be installed and wired by persons qualified and certified to perform the installation of fire alarm systems.

  - Provide suitable raceway system and wiring for complete system.

  - Install all components per manufacturer's recommendations, and co-ordination with the installation schedule.

  - Connect flow switches and supervisory switches for sprinkler, standpipe, and fire pump to fire alarm system (switches supplied by Fire Protection contractor).

  - Connect duct smoke detectors (supplied by this division, installed by HVAC contractor).

  - Where the duct smoke detector is not readily visible, mount duct smoke detector remote indicator in a visible and accessible location.

  - Where a duct mounted smoke detector is located on the roof, provide a weatherproof enclosure, equipped with a heater c/w built-in thermostat and power connection from the nearest DGP.

  - Remote Indicator and Remote Test Stations shall have an identifying label attached to the front of the cover plate listing the device served.

  - Where fire alarm devices are installed outdoors or in damp locations, they shall be protected from moisture and direct water spray, or designed for outdoor applications.

  - Where the control panel and/or associated equipment is located in a sprinklered room, the cabinet shall be provided with protection against flow from sprinkler heads.

  - All boxes and cabinets shall be listed for their intended purpose.

  - Devices installed during construction will be protected from dust, dirt, and paint.

  - Dust protection shall be removed upon completion of the verification.

## Wiring

  - Use solid copper conductors and size wiring to in accordance with manufacturer’s recommendations. Protect from mechanical injury or other conditions such as moisture, excessive heat or corrosive action to Class 1 requirements.

## Factory Rack Up and Testing

  - Manufacturer shall factory assemble and test all Network Panels, and Annunciators, prior to delivery to site.

  - Upon completion of the factory assembly and testing, a written notification confirming satisfactory completion of the testing shall be issued to the Owner’s Representative.

  - The Owner's representative will be notified in writing for witness testing to confirm the correct operation as per the Plans and Specifications prior to release for shipment to site, at the option of the Owner’s Representative.

## Testing, Inspection, Verification

  - The fire alarm system shall be verified in accordance to the latest revision of CAN/ULC-S537 “Standard for the Verification of Fire Alarm Systems”.

  - The verification shall include a complete inspection of all components installed to ensure the following:

    - That the system is complete in accordance with Specifications.

    - That the system is connected in accordance with Manufacturer's recommendations.

  - Adjust system and components as required to ensure complete system operation.

  - Where partial occupancies occur, the fire alarm system for the area to be occupied (including control units, annunciators, etc.) shall be tested and meet the requirements noted above.

  - After the testing and verification is completed, and all deficiencies rectified, notify the Engineers and representatives of the Fire/ Building Department and demonstrate the proper functioning of the system.

Training

  - The manufacturer shall provide to the Owner and include such costs to provide for a minimum two (2) in factory training or on Site sessions (at Owner's choice) of Owner's designated personnel (for up to 10 people each session) on the operation and maintenance procedures with regards to the respective systems.

  - The manufacturer shall allow for training sessions of a minimum four (4) hours each.

  - Schedule training with the Owner at least seven days in advance.

  - Training will be provided upon Partial Occupancy, where applicable, in addition to being provided upon final completion. The contractor shall include all costs for training upon Partial Occupancy.

  - Training shall be based on the Operation and Maintenance Manual.

Operating Instructions

  - Provide printed, simple operating instructions, acceptable to the Engineer, framed and mounted adjacent to the CACF.

End of Section